## AllRopePulleyPTO
Sub-system | Component | Annual Failure Rate | Part | Failure rate ratio for parts | Failure mode | Annual failure rate | Failure Mechanism | Annual failure rate due to the failure mechanism | Occurance (O) | Manhour repair | Severity (S) | Risk priority | Failure effect ranking | Criticality number | Summary | Note & Recommendation
Rope & Pulley PTO | Belt | 0.17287 | Belt | 1 | Deformation | 0.017287 | Fatigue | 0.030251 | 4 |  | 1 | 4 | 3 | 0.20744 | Dominant failure modes: Surface damage Dominant failure mechanism: Wear followed equally by Fatigue and Creep failure mechanism | Risk: Low to medium risk for all failure modes of the component's parts Criticality: Surface damage failrue mode followed by Separation failure mode for all parts of the component Recommendation: Ensure sufficient lubrication (e.g. by adapting an axilary lubraication system)
[5 empty] | Fracture/Separation | 0.05186 | Wear | 0.043216 | 4 |  | 1 | 4 | 3 | 0.62232
[5 empty] | Surface Damage | 0.10372 | Creep | 0.030251 | 5 |  | 1 | 5 | 2 | 1.0372
[7 empty] | UV Radiation | 0.017287
[7 empty] | Misalignment | 0.017287
[7 empty] | Corrosion | 0.017287
[7 empty] | Contamination ingress | 0.017287
|  | Sum |  | 1 |  | 0.17287 |  | 0.17287 | [5 empty] | 1.8669
| Pulley | 0.035345 | Pulley | 1 | Deformation | 0.0017672 | Fatigue | 0.0088361 | 3 |  | 2 | 6 | 3 | 0.03181 | Dominant failure mode(s): Surface damage Dominant failure mechanism(s): Wear followed by Fatigue
[5 empty] | Fracture/Separation | 0.0088361 | Wear | 0.012371 | 3 |  | 2 | 6 | 3 | 0.15905
[5 empty] | Surface Damage | 0.024741 | Misalignment | 0.0035345 | 4 |  | 2 | 8 | 2 | 0.39586
[7 empty] | Corrosion | 0.0053017
[7 empty] | Foreign Material | 0.0053017
|  | Sum |  | 1 |  | 0.035345 |  | 0.035345 | [5 empty] | 0.58672
| Rotary bearing unit | 0.049616 | Spherical Bearing | 0.7025 | Deformation | 0.0049616 | Fatigue | 0.012404 | 3 |  | 2 | 6 | 3 | 0.089308 | Dominant failure mode(s): Surface damage Dominant failure mechanism(s): Wear followed by Fatigue failure mechanism
|  |  | Seal | 0.2075 | Fracture/Separation | 0.0099231 | Wear | 0.017365 | 3 |  | 2 | 6 | 3 | 0.17862
|  |  | Housing | 0.09 | Surface Damage | 0.034731 | Misalignment | 0.0049616 | 4 |  | 2 | 8 | 2 | 0.55569
[7 empty] | Corrosion | 0.0049616
[7 empty] | Vibration | 0.0049616
[7 empty] | Lubrication Failed | 0.0024808
[7 empty] | Current Path (Spark) | 0.00049616
[7 empty] | Contamination ingress | 0.0024808
|  | Sum |  | 1 |  | 0.049616 |  | 0.050112 | [5 empty] | 0.82362
| Shaft | 0.012448 | Shaft | 1 | Deformation | 0.0024895 | Fatigue | 0.0043567 | 3 |  | 2 | 6 | 3 | 0.044812 | Dominant failure mode(s): Surface damage Most common failure mechanism(s): Fatigue followed equally by Corrosion and Wear failure meachanims
[5 empty] | Fracture/Separation | 0.0037343 | Wear | 0.0024895 | 3 |  | 2 | 6 | 3 | 0.067218
[5 empty] | Surface Damage | 0.0062239 | Misalignment | 0.0012448 | 3 |  | 2 | 6 | 2 | 0.074686
[7 empty] | Corrosion | 0.0024895
[7 empty] | Vibration | 0.0018672
|  | Sum |  | 1 |  | 0.012448 |  | 0.012448 | [5 empty] | 0.1419

## AllBallScrewPTO
Sub-system | Component | Annual Failure Rate | Part | Failure rate ratio for parts | Failure mode | Annual failure rate | FailureMechanism | Annual failure rate due to the failure mechanism | Occurance (O) | Manhour repair | Severity (S) | Risk priority (O*S) | Failure effect | Criticality number | Summary | Recommendation
Ball Screw PTO | Screw nut assembly | 0.10138 | Thrust Bearing | 0.034874 | Deformation | 0.0040552 | Fatigue | 0.025345 | 3 |  | 3 | 9 | 3 | 0.10949 | Most common part failure: Thrust bearing, Worm Wheel Most common failure mode(s): Fracture/separation Most common failure mechanism(s): Fatigue, Foreign material, Wear | An annual failure rate of 0.27 for a generic Ball Screw PTO. Medium risk for all components. Higher criticality numbers for the failure modes of fracture and surface damage in the FMECA result.
|  |  | Nut Screw | 0.0037713 | Fracture/Separation | 0.06691 | Wear | 0.014193 | 4 |  | 3 | 12 | 3 | 2.4088
|  |  | Worm Wheel | 0.033577 | Surface Damage | 0.030414 | Misalignment | 0.010138 | 4 |  | 3 | 12 | 2 | 0.72993
|  |  | Seals | 0.010401 |  |  | Corrosion | 0.010138
|  |  | Balls | 0.014376 |  |  | Foreign Material | 0.025345
|  |  | Housing | 0.0043796 |  |  | Lubrication Failure | 0.0050689
[7 empty] | Current Path(Spark) | 0.0010138
[7 empty] | Vibration | 0.010138
|  | Sum |  | 1 |  | 0.10138 |  | 0.17287 | [5 empty] | 3.2482
| Gear | 0.049703 | Gear | 1 | Deformation | 0.0019881 | Fatigue | 0.012426 | 3 |  | 2 | 6 | 3 | 0.035786 | Most common failure mode(s): Surface damage Most common failure mechanism(s): Fatigue, Foreign material
[5 empty] | Fracture/Separation | 0.032804 | Wear | 0.0069585 | 4 |  | 2 | 8 | 3 | 0.7873
[5 empty] | Surface Damage | 0.014911 | Misalignment | 0.0049703 | 4 |  | 2 | 8 | 2 | 0.23858
[7 empty] | Corrosion | 0.0049703
[7 empty] | Foreign Material | 0.012426
[7 empty] | Lubrication Failure | 0.0024852
[7 empty] | Current Path(Spark) | 0.00049703
[7 empty] | Vibration | 0.0049703
|  | Sum |  | 1 |  | 0.035345 |  | 0.035345 | [5 empty] | 0.58672
| Screw and rail assembly | 0.10138 | Screw | 0.1761 | Deformation | 0.0024895 | Fatigue | 0.0062239 | 3 |  | 2 | 6 | 3 | 0.044812 | Most common part failure: Rotary bearing Most common failure mode(s): Surface damage Most common failure mechanism(s): Wear, Fatigue
|  |  | Guide Rail | 0.1056 | Fracture/Separation | 0.0049791 | Wear | 0.0087134 | 3 |  | 2 | 6 | 3 | 0.089624
|  |  | Housing | 0.1408 | Surface Damage | 0.017427 | Misalignment | 0.0024895 | 4 |  | 2 | 8 | 2 | 0.27883
|  |  | Rortary Bearing | 0.5775 |  |  | Corrosion | 0.0024895
[7 empty] | Vibration | 0.0024895
[7 empty] | Lubrication Failed | 0.0012448
[7 empty] | Current Path (Spark) | 0.00024895
[7 empty] | Contamination ingress | 0.0012448
|  | Sum |  | 1 |  | 0.024895 |  | 0.025144 | [5 empty] | 0.41326
| Shaft | 0.012448 | Shaft | 1 | Deformation | 0.0024895 | Fatigue | 0.0043567 | 3 |  | 2 | 6 | 3 | 0.044812 | Most common part failure: Shaft Dominant failure modes: Surface damage, Fracture/separation Dominant failure mechanism: Wear, Fatigue
[5 empty] | Fracture/Separation | 0.0037343 | Wear | 0.0024895 | 3 |  | 2 | 6 | 3 | 0.067218
[5 empty] | Surface Damage | 0.0062239 | Misalignment | 0.0012448 | 3 |  | 2 | 6 | 2 | 0.074686
[7 empty] | Corrosion | 0.0024895
[7 empty] | Vibration | 0.0018672
|  | Sum |  | 1 |  | 0.012448 |  | 0.012448 | [5 empty] | 0.1419

## AllRack&PinionPTO
Sub-system | Component | Annual Failure Rate | Part | Failure rate ratio for parts | Failure mode | Annual failure rate | FailureMechanism | Annual failure rate due to the failure mechanism | Occurance (O) | Manhour repair | Severity (S) | Risk priority (O*S) | Failure effect ranking | Criticality number | Summary | Conclusion /Recommendation
Rack & Pinion PTO | Rotary bearing unit | 0.049616 | Spherical Bearing | 0.7025 | Deformation | 0.0049616 | Fatigue | 0.012404 | 3 |  | 2 | 6 | 3 | 0.089308 | Most common part(s) failure: Spherial bearing Most common failure modes: Surface damage Most common failure mechanism: Wear, Fatigue | An annual failure rate of 0.25 for a generic Rack & Pinion PTO. Rack and Pinion PTO lies in a medium risk category range of 6 to 12 (orange colour) for all its components. However, Rail assembly compoenent is in the border toward a red color risk category. The Rail assembly component, in particular, Bearing Rail and Rack Gear component got the highest criticality number in the FMECA result.
|  |  | Seal | 0.2075 | Fracture/Separation | 0.0099231 | Wear | 0.017365 | 3 |  | 2 | 6 | 3 | 0.17862
|  |  | Housing | 0.09 | Surface Damage | 0.034731 | Misalignment | 0.0049616 | 4 |  | 2 | 8 | 2 | 0.55569
[7 empty] | Corrosion | 0.0049616
[7 empty] | Vibration | 0.0049616
[7 empty] | Lubrication Failed | 0.0024808
[7 empty] | Current Path (Spark) | 0.00049616
[7 empty] | Contamination ingress | 0.0024808
|  | Sum |  | 1 |  | 0.049616 |  | 0.050112 | [5 empty] | 0.82362
| Gear | 0.049703 | Gear | 1 | Deformation | 0.0019881 | Fatigue | 0.012426 | 3 |  | 2 | 6 | 3 | 0.035786 | Most common failure mode(s): Fracture Most common failure mechanism(s): Fatigue, Foreign material
[5 empty] | Fracture/Separation | 0.032804 | Wear | 0.0069585 | 4 |  | 2 | 8 | 3 | 0.7873
[5 empty] | Surface Damage | 0.014911 | Misalignment | 0.0049703 | 4 |  | 2 | 8 | 2 | 0.23858
[7 empty] | Corrosion | 0.0049703
[7 empty] | Foreign Material | 0.012426
[7 empty] | Lubrication Failure | 0.0024852
[7 empty] | Current Path(Spark) | 0.00049703
[7 empty] | Vibration | 0.0049703
|  | Sum |  | 1 |  | 0.049703 |  | 0.049703 | [5 empty] | 1.0617
| Linear bearing unit | 0.028752 | Balls | 0.014376 | Deformation | 0.0028752 | Fatigue | 0.0071881 | 3 |  | 2 | 6 | 3 | 0.051754 | Most common part(s) failure: Balls Most common failure mode(s): Surface damage Dominant failure mechanism(s): Wear, Fatigue
|  |  | Seal | 0.010351 | Fracture/Separation | 0.0057505 | Wear | 0.010063 | 3 |  | 2 | 6 | 3 | 0.10351
|  |  | Housing | 0.0040253 | Surface Damage | 0.020127 | Misalignment | 0.0028752 | 4 |  | 2 | 8 | 2 | 0.32203
[7 empty] | Corrosion | 0.0028752
[7 empty] | Vibration | 0.0028752
[7 empty] | Lubrication Failed | 0
[7 empty] | Current Path (Spark) | 0.00028752
[7 empty] | Contamination ingress | 0.0011501
|  | Sum |  | 0.028752 |  | 0.028752 |  | 0.027315 | [5 empty] | 0.47729
| Shaft | 0.012448 | Shaft | 1 | Deformation | 0.0024895 | Fatigue | 0.0043567 | 3 |  | 2 | 6 | 3 | 0.044812 | Dominant failure mode(s): Surface damage Dominant failure mechanism(s): Fatigue
[5 empty] | Fracture/Separation | 0.0037343 | Wear | 0.0024895 | 3 |  | 2 | 6 | 3 | 0.067218
[5 empty] | Surface Damage | 0.0062239 | Misalignment | 0.0012448 | 3 |  | 2 | 6 | 2 | 0.074686
[7 empty] | Corrosion | 0.0024895
[7 empty] | Vibration | 0.0018672
|  | Sum |  | 1 |  | 0.012448 |  | 0.012448 | [5 empty] | 0.1419
| Rail Assembly | 0.11045 | Rack Beam | 0.0055226 | Deformation | 0.0044181 | Fatigue | 0.027613 | 3 |  | 3 | 9 | 3 | 0.11929 | Most common parts failure: Bearing rail, Rack gear Dominant failure modes: Fracture Dominant failure mechanism: Fatigue, Foreign material
|  |  | Bearing Rail | 0.049703 | Fracture/Separation | 0.072898 | Wear | 0.015463 | 4 |  | 3 | 12 | 3 | 2.6243
|  |  | End Stop Bumper | 0.0055226 | Surface Damage | 0.033135 | Misalignment | 0.011045 | 4 |  | 3 | 12 | 2 | 0.79525
|  |  | Rack Gear | 0.049703 |  |  | Corrosion | 0.011045
[7 empty] | Foreign Material | 0.027613
[7 empty] | Lubrication Failure | 0.0055226
[7 empty] | Current Path(Spark) | 0.0011045
[7 empty] | Vibration | 0.011045
|  | Sum |  | 0.11045 |  | 0.11045 |  | 0.11045 | [5 empty] | 3.5389

## AllHydraulicPTO w Ele.Generat
Sub-system | Component | Annual Failure Rate | Part | Failure rate ratio for parts | Failure mode | Annual failure rate | FailureMechanism | Annual failure rate due to the failure mechanism | Occurance (O) | Manhour repair | Severity (S) | Risk priority (O*S) | Failure effecct ranking | Criticality number | Summary (Part, Failure modes, Failure mechnisms) | Conclusion/ Remarkds
HYDRAULIC PTO | Hydraulic linear actuator | 0.39035 | Piston | 0.0097587 | External Leakage | 0.097587 | Excessive Side Load | 0.012404 | 4 |  | 2 | 8 | 3 | 2.3421 | Most common part(s) failure: Seals, Clevis, Bearing Most common failure mechanism(s): Seals failure, Rod corrosion | Risk: Medium risks for all failure modes Criticality: External and Internal Leakage have the highest criticality numbers followed by Bearing failure failure mode. Spurious Position Change failure mode and Jamming have the lowest criticality numbers. Recomendation: Maintain Hydraulic Seals
|  |  | Cylinder | 0.0097587 | Internal Leakage | 0.097587 | Seals Failure | 0.017365 | 4 |  | 2 | 8 | 3 | 2.3421
|  |  | Rod | 0.039035 | Spurious Position Change | 0.0039035 | Rod Corrosion | 0.0049616 | 3 |  | 2 | 6 | 2 | 0.046842
|  |  | Clevis | 0.097587 | Jamming | 0.0039035 | Fatigue | 0.0049616 | 3 |  | 2 | 6 | 3 | 0.046842
|  |  | Seals | 0.13662 | Aeration | 0.054649 | Contamination | 0.0049616 | 4 |  | 2 | 8 | 2 | 0.87438
|  |  | Bearing | 0.097587 | Mechanical Failure | 0.054649 | High Pressure | 0.0024808 | 4 |  | 2 | 8 | 3 | 1.3116
[5 empty] | Bearing Failure | 0.07807 |  | 0.00049616 | 4 |  | 2 | 8 | 3 | 1.8737
0.0024808
|  | Sum |  | 0.39035 |  | 0.39035 |  | 0.050112 | [5 empty] | 8.8375
| Valves (general) | 0.337 | Actuating device | 0.0043 | Abnormal instrument reading | 0.03628 | Clearance/alignment failure | 0.0014498 | 4 | 5.6212 | 2 | 8 | 1 | 0.29024 | Dominant failure mode(s): Internal and external leakage, Fail to open on demand Dominant failure mechanism(s): Leakage | Annual failure rate of 0.337 for generic valves. OREDA database is mainly for oil and gas industires that operate in extreme environmental conditions. It is expected that the failure rate of valves is lower for the WECs. For instance literautre provides an annual failure rate of 0.20 for relief valves and 0.05 for the check valves (Neary et al., 2014) and mean annual failure rate of 0.02 for general failure of non-return valve (Thies, 2012). Risks: In general valves show a low to medium risks for all failure modes except the failure modes related to leakages. Criticality: Most critical failure modes are 'External and Interal leakage' and Instrument
|  |  | Bonnet | 0.0043 | Delayed operation | 0.017603 | Combined causes | 0.0028996 | 4 | 82.2583 | 4 | 16 | 2 | 0.56331
|  |  | Closure member(ball/gate/disc.etc) | 0.0515 | External leakage- Process medium | 0.060634 | Contamination | 0.0014498 | 4 | 43.3046 | 4 | 16 | 3 | 2.9104
|  |  | Control unit | 0.0086 | External leakage- utility medium | 0.05325 | Control failure | 0.0028996 | 4 | 43.495 | 4 | 16 | 3 | 2.556
|  |  | Flange | 0.0043 | Fail to close on demand | 0.0074985 | Corrosion | 0.014498 | 3 | 2.575 | 1 | 3 | 2 | 0.044991
|  |  | Instrument, general | 0.0343 | Fail to open on demand | 0.057063 | Deformation | 0.0014498 | 4 | 55.9062 | 4 | 16 | 2 | 1.826
|  |  | Instrument, position | 0.0086 | Fail to regulate | 0.003739 | Electrical failure-general | 0.0057992 | 3 | 0.29167 | 1 | 3 | 2 | 0.022434
|  |  | Monitoring | 0.0089 | Interal leakage | 0.023838 | Faulty signal/indication/alarm | 0.015982 | 4 | 58.0412 | 4 | 16 | 3 | 1.1442
|  |  | Other | 0.0215 | Minor in-service problems | 0.030126 | Instrument failure-genera | 0.018848 | 4 | 12.9375 | 3 | 12 | 1 | 0.36151
|  |  | Other actuator components | 0.0215 | other | 0.016596 | Leakage | 0.10027 | 4 | 22.0829 | 3 | 12 | 2 | 0.3983
|  |  | Other valve component | 0.0215 | Spurious operation | 0.014002 | Losseness | 0.0043494 | 4 | 4.7488 | 2 | 8 | 2 | 0.22403
|  |  | Packing | 0.0215 | Structural deficiency | 0.0074283 | Material failure-general | 0.015948 | 3 | 1.875 | 1 | 3 | 3 | 0.066855
|  |  | Pilot valve | 0.0086 | Unknown | 0.0042405 | Mechanical failure-general | 0.042078 | 3 | 1.3058 | 1 | 3 | 2 | 0.025443
|  |  | Seals | 0.0387 | Valve leakage in closed position | 0.0048682 | Miscellaneous-general | 0.0028996 | 3 | 4.4167 | 2 | 6 | 3 | 0.087628
|  |  | Seals (gaskets) | 0.0301 |  |  | No cause found | 0.0072828
|  |  | Spring | 0.0043 |  |  | No signal/indicaiton/alarm | 0.0014498
|  |  | Stem | 0.0043 |  |  | Other | 0.0072491
|  |  | Subunit | 0.1032 |  |  | Out of adjustment | 0.014532
|  |  | Unkown | 0.5795 |  |  | Stichking | 0.0086989
|  |  | Valve body with inernals | 0.0215 |  |  | Unknown | 0.065376
[7 empty] | Wear | 0.0014498
|  | Sum |  | 1.001 |  | 0.33717 |  | 0.33686 | [5 empty] | 10.5214
HYDRAULIC PTO | Filter | 0.28577 | Housing | 0.05 | Abnormal Instrument Reading | 0.057154 | Blocked/Plugged | 0.14289 | 4 |  | 2 | 8 | 3 | 1.3717 | Most common part failure: Balls Dominant failure modes: Surface damage Dominant failure mechanism: Wear, Fatigue | Risk: Medium risks for all failure modes Criticality: Fail to clean has the highest criticality numbers followed by External leakage.
|  |  | Filter Element | 0.5 | External Leakage | 0.085731 | Material Failure | 0.057154 | 4 |  | 2 | 8 | 3 | 2.0576
|  |  | Seals | 0.3 | Fail to Clean | 0.14289 | Instrument Failure | 0.028577 | 5 |  | 2 | 10 | 2 | 2.8577
|  |  | Bypass Valve | 0.05 |  |  | Looseness | 0.028577
|  |  | Instrument | 0.1 |  |  | Leakage | 0.028577
|  | Sum |  | 1 |  | 0.28577 |  | 0.28577 | [5 empty] | 6.287
| Manifold (connector & Valve isolation) | 0.019455 | Connector | 0.33333 | External leakage- Process medium | 0.019455 | Losseness | 0.0064849 | 4 | 0.16667 | 1 | 4 | 3 | 0.23346 | Most common part(s) part fialure: Valve isolation Critical failure modes: External leakage Dominant failure mechanism: Wear | Risk: low Criticality: low
|  |  | Valve, process isolation | 0.66667 |  |  | Wear | 0.01297
|  | Sum |  | 1 |  | 0.019455 |  | 0.019455 | [5 empty] | 0.23346
| Reciprocating pump | 0.84548 | Actuating device | 0.0133 | Abnormal instrument reading | 0.01083 | Blockage/plugged | 0.011341 | 4 | 0.16667 | 1 | 4 | 1 | 0.043318 | Common part(s) failure: Subunit, Casting, Oil, Seals Most failure mode(s): External & internal leakage, Breakdown, Parameter deviation Most failure mechanism(s): Wear, Material failure, Leakage | Risk: Low to medium risks for all failure modes except Breakage and Leakage that are in the high risk category area. Criticality: External leakage (process) has the highest criticality number followed by Breakdown failure mode.
|  |  | Casting | 0.12 | Breakdown | 0.11723 | Breakage | 0.04545 | 5 | 27.2083 | 3 | 15 | 3 | 5.2755
|  |  | Coupling to driven unit | 0.0133 | Erratic output | 0.057504 | Burst | 0.022768 | 4 | 13.3758 | 2 | 8 | 3 | 1.3801
|  |  | Coupling to driver | 0.0266 | External leakage-process | 0.15827 | Clearance/alignment | 0.022682 | 5 | 31.635 | 3 | 15 | 3 | 7.1222
|  |  | Cylinder liner | 0.04 | Eternal leakage- Utility medium | 0.078735 | Faulty signal/indication/alarm | 0.022682 | 4 | 6.0408 | 3 | 12 | 3 | 2.8345
|  |  | Diaphragm | 0.0533 | Fail to star on demand | 0.011071 | Leakage | 0.13644 | 4 | 0.25 | 3 | 12 | 2 | 0.26569
|  |  | Filter(s) | 0.04 | Internal leakage | 0.035613 | Losseness | 0.022682 | 4 | 17.5417 | 3 | 12 | 3 | 1.2821
|  |  | Gearbox/var.drive | 0.04 | Low output | 0.029744 | Material failure-general | 0.13635 | 4 | 1.5 | 2 | 8 | 2 | 0.47591
|  |  | Instrument, pressure | 0.0266 | Minor in-service problems | 0.011071 | Mechanical failure-general | 0.068218 | 4 | 0.041667 | 1 | 4 | 1 | 0.044282
|  |  | Lubrication | 0.0133 | Noise | 0.048255 | Miscellaneous- general | 0.034109 | 4 | 16.5538 | 2 | 8 | 2 | 0.77208
|  |  | Oil | 0.0933 | other | 0.079302 | No cause found | 0.011341 | 4 | 2.1667 | 2 | 8 | 2 | 1.2688
|  |  | Other | 0.0399 | Parameter deviation | 0.1081 | Other | 0.011341 | 5 | 22.7 | 2 | 10 | 2 | 2.1621
|  |  | Piston(s) | 0.0266 | Plugged/chocked | 0.01083 | Overheating | 0.011341 | 4 | 0.16667 | 3 | 12 | 3 | 0.38986
|  |  | Pulsation damper | 0.0533 | Spurious stop | 0.01318 | Unknown | 0.022682 | 4 | 0.25 | 3 | 12 | 3 | 0.4745
|  |  | Seals | 0.0934 | Vibration | 0.08298 | Vibration | 0.011341 | 4 | 8.9992 | 2 | 8 | 3 | 1.9915
|  |  | Subunit | 0.1467 |  |  | Wear | 0.26153
|  |  | Thrust bearing | 0.0133
|  |  | Unkown | 0.0666
|  |  | Valves | 0.08
|  | Sum |  | 0.9995 |  | 0.85272 |  | 0.8523 | [5 empty] | 25.7824
HYDRAULIC PTO | Centrifugal Pump | 1.4648 | Actuating device | 0.0066 | Abnormal instrument reading | 0.37601 | Blockage/plugged | 0.088915 | 5 | 0.53384 | 1 | 5 | 1 | 1.88 | Common part(s) failure: Insrument Most common failure mode(s): Abnormal instrument reading, External & internal leakage Most failure mechanism(s): Leakage | Annual failure rate of 0.337 for generic valves. OREDA database is mainly for oil and gas industires that operate in extreme environmental conditions. It is expected that the failure S100:S107rate of valves is lower for the WECs. For instance the annual failure rate of 0.20 for relief valves and 0.05 for the check valves (Neary et al., 2014) and mean annual failure rate of 0.02 for general failure of non-return valve (Thies, 2012). Risks: In general valves show a low to medium risks for all failure modes except the failure modes related to leakages. For recommendation see paper Sotoudeh, 2021. Criticality: Most critical failure modes are 'External and Interal leakage' and Instrument
|  |  | Casing | 0.0077 | Breakdown | 0.01628 | Breakage | 0.015967 | 4 | 6.1659 | 2 | 8 | 3 | 0.13024
|  |  | Control unit | 0.028 | Erratic output | 0.017 | Cleanrance/alignment failure | 0.027539 | 4 | 0.505 | 1 | 4 | 3 | 0.068001
|  |  | Cooler(s) | 0.0125 | External leakage-process | 0.20726 | Contamination | 0.049804 | 5 | 2.3744 | 1 | 5 | 3 | 1.0363
|  |  | Colling/heating system | 0.0113 | External leakage- utility | 0.22475 | Control failure | 0.029297 | 5 | 1.3913 | 1 | 5 | 3 | 1.1237
|  |  | Coupling to driver | 0.0066 | Fail to star on demand | 0.024201 | Corrosion | 0.046288 | 4 | 4.6379 | 2 | 8 | 2 | 0.19361
|  |  | Filter(s) | 0.012 | Fail to stop | 0.0026882 | Erosion | 0.029297 | 3 | 0.60083 | 1 | 3 | 2 | 0.0080645
|  |  | Filter, cyclone | 0.0089 | High output | 0.0057691 | Faulty signal/indication/alarm | 0.17153 | 3 | 4.6848 | 2 | 6 | 2 | 0.034614
|  |  | Gearbox/var.drive | 0.0054 | Internal leakage | 0.042684 | Instrument failure-genral | 0.076464 | 4 | 1.8296 | 1 | 4 | 3 | 0.17073
|  |  | Impeller | 0.0072 | Low output | 0.021869 | Leakage | 0.28711 | 4 | 1.5886 | 1 | 4 | 2 | 0.087474
|  |  | Instrument | 0.2495 | Minor in service problem | 0.10777 | Looseness | 0.025781 | 5 | 0.73055 | 1 | 5 | 1 | 0.53887
|  |  | Monitoring | 0.0119 | Noise | 0.0092628 | Material failure-general | 0.02666 | 3 | 1.2692 | 1 | 3 | 2 | 0.027788
|  |  | Oil | 0.0445 | Overheating | 0.027644 | Mechanical failure-general | 0.13154 | 4 | 2.2995 | 1 | 4 | 3 | 0.11058
|  |  | Other | 0.1007 | Parameter deviatio | 0.053048 | No signal/indication/alarm | 0.050683 | 4 | 1.1079 | 1 | 4 | 2 | 0.21219
|  |  | Piping | 0.0475 | Plugged/chocked | 0.024604 | Out of adjustment | 0.062255 | 4 | 0.55266 | 1 | 4 | 3 | 0.098417
|  |  | Pump | 0.0066 | Spurious stop | 0.036101 | Vibration | 0.047167 | 4 | 2.0058 | 1 | 4 | 2 | 0.1444
|  |  | Purge air | 0.0072 | Structrual deficiency | 0.022217 | Wear | 0.11206 | 4 | 2.7681 | 1 | 4 | 3 | 0.088868
|  |  | Radial bearing | 0.0155 | Unknown | 0.015322 | Other | 0.09 | 4 | 1.375 | 1 | 4 | 2 | 0.061289
|  |  | Seals | 0.1328 | Vibration | 0.076481 | Unknown | 0.095067 | 4 | 2.9285 | 2 | 8 | 3 | 0.61185
|  |  | Subunit | 0.041 | Other | 0.15386 |  |  | 5 | 1.2938 | 1 | 5 | 2 | 0.76929
|  |  | Thrust bearing | 0.0161
|  |  | Unknown | 0.1508
|  |  | Valves | 0.0676
|  | Sum |  | 0.9979 |  | 1.4648 |  | 1.4634 | [5 empty] | 7.3964
| Piston Accumulator | 0.33539 | Pressure Vessel | 0.01 | External Leakage | 0.083847 | Contamination | 0.083847 | 4 |  | 1 | 4 | 3 | 1.0062 | Most common part(s) failure: Seal Most common failure mod(s): Pressure loss, Gas & Oil mixture Most common failure mechanism(s): Leakage | Risk: Low risks for failure modes Criticality: The failure mode of pressure loss has the highest criticality number
|  |  | Piston | 0.05 | Cylinder Damage | 0.0033539 | Wear | 0.016769 | 3 |  | 1 | 3 | 2 | 0.020123
|  |  | Oil Valve | 0.275 | Pressure Loss | 0.11739 | Corrosion | 0.016769 | 5 |  | 1 | 5 | 2 | 1.1739
|  |  | Gas Valve | 0.275 | Gas & Oil Mixture | 0.10062 | Piston Jammed | 0.083847 | 5 |  | 1 | 5 | 2 | 1.0062
|  |  | Seal | 0.39 | Breakdown | 0.030185 | Jammed Valve | 0.016769 | 4 |  | 1 | 4 | 3 | 0.36222
[7 empty] | Leakage | 0.11739
|  | Sum |  | 1 |  | 0.33539 |  | 0.33539 | [5 empty] | 3.5685
| Bladder Accumlator | 0.33539 | Pressure Vessel | 0.01 | External Leakage | 0.083847 | Contamination | 0.083847 | 4 |  | 1 | 4 | 3 | 1.0062 | Most common part(s) failure: Oil & Gas Valves Most common failure mod(s): Pressure loss Most common failure mechanism(s): Leakage | Risk: Low risks for failure modes Criticality: The failure mode of pressure loss has the highest criticality number
|  |  | Bladder | 0.2 | Cylinder Damage | 0.0033539 | Wear | 0.016769 | 3 |  | 1 | 3 | 2 | 0.020123
|  |  | Oil Valve | 0.275 | Pressure Loss | 0.16769 | Corrosion | 0.016769 | 5 |  | 1 | 5 | 2 | 1.6769
|  |  | Gas Valve | 0.275 | Gas & Oil Mixture | 0.050308 | Failed Bladder | 0.067077 | 4 |  | 1 | 4 | 2 | 0.40246
|  |  | Seal | 0.24 | Breakdown | 0.030185 | Jammed Valve | 0.016769 | 4 |  | 1 | 4 | 3 | 0.36222
[7 empty] | Leakage | 0.13415
|  | Sum |  | 1 |  | 0.33539 |  | 0.33539 | [5 empty] | 3.4679
| Heat Exchanger (generic) | 0.29708 | Body/shell | 0.0462 | Abnormal instrument reading | 0.073606 | Blockage/plugged | 0.045892 | 4 | 24.9129 | 3 | 12 | 1 | 0.88327 | Most common failure mod(s): Abnormal instrument reading mixture Most common failure mechanism(s): Blockage | Risk: Medium to high risks for all failure modes. Criticality: Failure mode of Internal leakage has the highest criticality number followed by the failure mode of Insufficient heat transfer.
|  |  | Control unit | 0.0084 | External leakage process medium | 0.035012 | Breakage | 0.0089235 | 4 | 44.0404 | 4 | 16 | 3 | 1.6806
|  |  | Instrument, flow | 0.0168 | External leage- utility medium | 0.018227 | Control failure | 0.014023 | 4 | 19.7454 | 3 | 12 | 3 | 0.65616
|  |  | Instrument, level | 0.0126 | Insufficient heat transfer | 0.049802 | Corrosion | 0.026771 | 4 | 102.1992 | 4 | 16 | 2 | 1.5937
|  |  | Instrument, pressure | 0.0966 | Internal leakage | 0.04564 | Faulty signal/indication-general | 0.026771 | 4 | 193.4542 | 5 | 20 | 3 | 2.7384
|  |  | Instrument, temperature | 0.0924 | Parameter deviation | 0.011033 | Instrument failure-general | 0.019122 | 4 | 23.0833 | 3 | 12 | 2 | 0.26478
|  |  | Other | 0.105 | Plugged/Chocked | 0.022276 | Leakage | 0.025496 | 4 | 23.8142 | 3 | 12 | 3 | 0.80192
|  |  | Piping | 0.0504 | Structural deficiency | 0.0065302 | Losseness | 0.012748 | 3 | 16.3083 | 3 | 9 | 3 | 0.17631
|  |  | Plates | 0.1134 | Minor in-service problems | 0.019157 | Material failure-general | 0.022946 | 4 | 14.2417 | 3 | 12 | 1 | 0.22989
|  |  | Seals (gaskets) | 0.0042 | Other | 0.02224 | Mechanical failure-general | 0.014023 | 4 | 166.1667 | 5 | 20 | 2 | 0.88961
|  |  | Subunit | 0.0378 |  |  | No signal/indication | 0.0063739
|  |  | Tubes | 0.0672 |  |  | Out of adjustment | 0.015297
|  |  | Unknown | 0.2856 |  |  | Wear | 0.0076487
[7 empty] | Other | 0.019
[7 empty] | Unknown | 0.039518
|  | Sum |  | 0.9366 |  | 0.30352 |  | 0.30455 | [5 empty] | 9.9145
Electric generator | Generator-motor dirven | 0.57416 | Control unit | 0.1764 | Abnormal instrument reading | 0.095378 | Blockage/plugged | 0.011253 | 4 | 5.3754 | 2 | 8 | 1 | 0.63048 | Most common part(s) failure: Unknown, Control unit Most common failure mode(s): Abnormal instrument reading, External leakage, Fail to synchronize, Faulty output voltage Most common failure mechanism(s): Unknown, Electrical failure (general), Faulty signal/indication | Risks: In general all failure modes are in the low to medium risk category matrix. Criticality: The failure mode with the highest criticality number is External leakage followed by the failure mode of Fail to synchronise
|  |  | Filter(s) | 0.0196 | External leakage Utility medium | 0.079444 | Combined causes | 0.011253 | 4 | 3.6458 | 2 | 8 | 3 | 1.5754
|  |  | Instrument, frequency | 0.0196 | Fail to start on demand | 0.039432 | Control failure | 0.03376 | 4 | 6.52 | 2 | 8 | 2 | 0.52131
|  |  | Instrument, general | 0.0196 | Fail to stop on demand | 0.02457 | Electrical failure-general | 0.090028 | 4 | 7.1667 | 2 | 8 | 2 | 0.32483
|  |  | Instrument, temperature | 0.1176 | Fail to synchronize | 0.07266 | External influence-general | 0.011253 | 4 | 8.625 | 3 | 12 | 2 | 1.4409
|  |  | Instrument, voltage | 0.0196 | Faulty output voltage | 0.074485 | Faulty power/voltage | 0.03376 | 4 | 7.4163 | 2 | 8 | 2 | 0.98474
|  |  | Monitoring | 0.0196 | Low output | 0.043937 | Faulty signal/indication/alarm | 0.090085 | 4 | 4.5 | 2 | 8 | 2 | 0.58087
|  |  | Other | 0.1176 | Minor in-service problems | 0.019044 | Instrument failure-genera | 0.067521 | 4 | 1.6667 | 1 | 4 | 1 | 0.062943
|  |  | Pump | 0.0196 | Other | 0.023343 | Leakage | 0.03376 | 4 | 1.7917 | 1 | 4 | 2 | 0.1543
|  |  | Subunit | 0.0196 | Overheating | 0.060384 | Mechanical failure-general | 0.011253 | 4 | 3.12 | 1 | 4 | 3 | 0.59873
|  |  | Unkown | 0.4312 | Parameter deviation | 0.01037 | No cause found | 0.011253 | 4 | 0.83333 | 1 | 4 | 2 | 0.06855
|  |  | Valves | 0.0196 | Structural deficiency | 0.01037 | No signal/indicaiton/alarm | 0.011253 | 4 | 0.79167 | 1 | 4 | 3 | 0.10282
[5 empty] | Unknown | 0.020738 | Overheating | 0.03376 | 4 | 0.22917 | 1 | 4 | 2 | 0.13709
[7 empty] | Unknown | 0.11253
[7 empty] | Vibration | 0.011253
|  | Sum |  | 0.9996 |  | 0.57416 |  | 0.57398 | [5 empty] | 7.183
| Generator Trubine driven | 0.72832 | Contril unit | 0.066 | Abnormal instrument reading | 0.13043 | Blockage/plugged | 0.020612 | 5 | 11.8013 | 3 | 15 | 1 | 1.9565 | Most common part(s) failure: Piping Most common failure mode(s): External leakage , Abnormal instrument reading, Minor in service propblem Most common failure mechanism(s): Electrical failure (general), Mechanical failure (general), Leakag, | Risks: In general The component has has a low to high risk. The failure modes of 'Breakage', 'External leakage' have the highest risk ranks while failure modes of 'Vibration' and 'Fail to cynchoronize' have the lower risk ranks. Criticality: Most critical failure mode is 'External leakage'.
|  |  | Excitation | 0.0848 | Breakage | 0.043066 | Breakage | 0.020539 | 4 | 361.3 | 5 | 20 | 3 | 2.584
|  |  | Fan | 0.0094 | External leakage utility medium | 0.20233 | Caviation | 0.0068463 | 5 | 45.7725 | 4 | 20 | 3 | 12.14
|  |  | Filter(s) | 0.0094 | Fails to start on demand | 0.014669 | Clearance/alighnement failure | 0.0068463 | 4 | 2.1667 | 1 | 4 | 2 | 0.11735
|  |  | Gearbox | 0.0471 | Fail to synchronize | 0.0070512 | Contamination | 0.013693 | 3 | 0.0041667 | 1 | 3 | 2 | 0.042307
|  |  | Heat exchanger | 0.0094 | Faulty output voltage | 0.04392 | Control failure | 0.020612 | 4 | 9.5838 | 3 | 12 | 2 | 1.0541
|  |  | Instrument, current | 0.0377 | Minor in-service problems | 0.10715 | Corrosion | 0.034377 | 5 | 4.505 | 3 | 15 | 1 | 1.6073
|  |  | Instrument, frequency | 0.0188 | Other | 0.036802 | Earth/isolation fault | 0.013765 | 4 | 144.2912 | 4 | 16 | 2 | 1.1777
|  |  | Instrument, general | 0.0188 | Overheating | 0.012741 | Electrical failure-general | 0.11685 | 4 | 1.0833 | 1 | 4 | 3 | 0.1529
|  |  | Instrument , temperature | 0.0472 | Parameter deviation | 0.086414 | Faulty power/voltage | 0.048069 | 4 | 10.52 | 3 | 12 | 2 | 2.0739
|  |  | Instrument, vibration | 0.0094 | Spurious stop | 0.021978 | Faulty signal/indication | 0.061835 | 4 | 3.4162 | 1 | 4 | 2 | 0.17582
|  |  | Instrument, voltage | 0.0377 | Structural deficiency | 0.014715 | Instrument failure-general | 0.03445 | 4 | 22 | 3 | 12 | 3 | 0.52972
|  |  | Monitroing | 0.0377 | Vibration | 0.0070512 | Leakage | 0.075527 | 3 | 0.0041667 | 1 | 3 | 2 | 0.042307
|  |  | Other | 0.066 |  |  | Looseness | 0.020612
|  |  | Piping | 0.1792 |  |  | Material failure-general | 0.061835
|  |  | Pump | 0.0188 |  |  | Mechanical failure-general | 0.068681
|  |  | Reserviou incl. heating | 0.0283 |  |  | No signal/indication/alarm | 0.020612
|  |  | Rotor | 0.0094 |  |  | Open circuit | 0.020612
|  |  | Seals | 0.0094 |  |  | Other | 0.0068463
|  |  | Stator | 0.0377 |  |  | Overheating | 0.0068463
|  |  | Subunit | 0.0471 |  |  | Software failure | 0.0068463
|  |  | Unknown | 0.066 |  |  | Unknown | 0.013693
|  |  | Valves | 0.0283 |  |  | Vibration | 0.013693
|  |  | Wirign | 0.0755 |  |  | Wear | 0.013693
|  | Sum |  | 0.9991 |  | 0.72832 |  | 0.72798 | [5 empty] | 23.6538
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Side loading occurs when a mass or external force pushes the rod to the side, up or down. from: https://www.fluidpowerworld.com/how-do-hydraulic-cylinders-fail-side-loads/#:~:text=Side%20loading%20occurs%20when%20a,itself%20inside%20the%20cylinder%20bore.

## All PowerTransmission & Control
Sub-system | Component | Annual Failure Rate | Part | Failure rate ratio for parts | Failure mode | Annual failure rate | FailureMechanism | Annual failure rate due to the failure mechanism | Occurance (O) | Manhour repair | Severity (S) | Risk priority (O*S) | Failure effect ranking | Criticality number | Summary (Part, Failure modes, Failure mechnisms) | Note & Recommendation
POWER TRANSMISSION & CONTROL | Frequency Converter (HV) | 1.4477 | Brake choppers | 0.0626 | Abnormal instrument reading | 0.0999 | Blockage/plugged | 0.049524 | 4 | 4 | 2 | 8 | 1 | 0.87624 | Most common part(s) failure: Pump Most common failure mode(s): Spurious stop followed by Fail to start on demand Most common failure mechanism(s): Unknown followed by Shor circuiting and Electrical failure-general | Risk: High risk for the failure mode of Electrical failure Criticality: The highest criticality number for Electrical failure mode followed by Sorious stop
|  |  | Communication cards | 0.0312 | Breakdown | 0.049975 | Breakage | 0.045169 | 4 | 0.64583 | 1 | 4 | 3 | 0.65751
|  |  | Control unit | 0.0312 | External leakage- Utility medium | 0.049975 | Combined causes | 0.045169 | 4 | 0.125 | 1 | 4 | 3 | 0.65751
|  |  | Enclosure fixtures and fittings | 0.0312 | Fail to function as intended | 0.09995 | Contamination | 0.045169 | 4 | 2.9583 | 1 | 4 | 2 | 0.87668
|  |  | Filter(s) | 0.0624 | Fail to function on demand | 0.099726 | Earth/isolation fault | 0.045169 | 4 | 0.5 | 1 | 4 | 3 | 1.3121
|  |  | Harmonic filter | 0.0313 | Fail to start on demand | 0.25 | Electrical failure- general | 0.13551 | 5 | 10.6042 | 3 | 15 | 3 | 12.3345
|  |  | Instrument, power | 0.0312 | Low output | 0.14965 | Faulty signal/indication/alarm | 0.045169 | 5 | 1.2083 | 1 | 5 | 2 | 1.6408
|  |  | Instrument, speed | 0.0624 | Minor in-service problems | 0.049975 | Instrument failure- general | 0.045169 | 4 | 1.0208 | 1 | 4 | 1 | 0.21917
|  |  | Internal circuit breaker or disconnector | 0.0313 | Noise | 0.049751 | Leakage | 0.090484 | 4 | 2.3333 | 1 | 4 | 3 | 0.65457
|  |  | Monitoring | 0.0624 | Other | 0.049975 | Looseness | 0.045169 | 4 | 0.75 | 1 | 4 | 2 | 0.43834
|  |  | Output filters | 0.0312 | Overheating | 0.049975 | Mechanical failure- general | 0.090339 | 4 | 1.7708 | 1 | 4 | 3 | 0.65751
|  |  | Piping | 0.0938 | parameter deviation | 0.0999 | No power/voltage | 0.045169 | 4 | 0.35417 | 1 | 4 | 2 | 0.87624
|  |  | Protective devices | 0.0312 | Spurious stop | 0.34898 | Open circuit | 0.045169 | 5 | 1.1458 | 1 | 5 | 3 | 5.7394
|  |  | Pump | 0.2189 |  |  | Out of adjustment | 0.045169
|  |  | Unknown | 0.0936 |  |  | Short circuiting | 0.18082
|  |  | Valves | 0.0624 |  |  | Software failure | 0.045169
|  |  | Wiring | 0.0312 |  |  | Unknown | 0.36179
[7 empty] | Wear | 0.045169
|  | Sum |  | 0.9995 |  | 1.4477 |  | 1.4505 | [5 empty] | 26.9406
| Switchgear (low voltage) | 0.94352 | Control power supply | 0.0588 | Faile to function as intended | 0.11099 | Breakage | 0.11096 | 5 | 2.1667 | 1 | 5 | 2 | 1.1097 | Most common part(s) failure: Motor starters and Peripheral Interfact control Most common failure mode(s): Other failure mode followed by Fail to funciton on demand Most common failure mechanism(s): Electrical failure | Risk: Low to medirum risk for all failure modes Criticality: The highest criticality number for Electrical failure mode followed by Sprious stop
|  |  | Earthing switch | 0.1176 | Fail to function on demand | 0.22188 | Earth/isolaton fault | 0.11096 | 5 | 0.43042 | 1 | 5 | 3 | 3.3278
|  |  | Interface cabinet | 0.1176 | Other | 0.44426 | Electrical failure-general | 0.27749 | 5 | 3.55 | 2 | 10 | 2 | 8.884
|  |  | Metering | 0.0588 | Sputious stop | 0.16639 | Faulty signal/indication/alarm | 0.16653 | 5 | 0.95833 | 1 | 5 | 3 | 2.4955
|  |  | Miniature circuit breaker | 0.0588 |  |  | Losseness | 0.055479
|  |  | Motor starters (contactor) | 0.2353 |  |  | Material failure- general | 0.055479
|  |  | Peripheral interface controler (PIC) | 0.2352 |  |  | No signal/indication/alarm | 0.11096
|  |  | Protection relay and interlock | 0.1176 |  |  | Sotfware failure | 0.055479
|  |  |  | 0.9997 |  | 0.94352 |  | 0.94333 | [5 empty] | 15.8171
POWER TRANSMISSION & CONTROL | Sensor | 0.0078748 | Pressure sensor | 1 | Control/signal failure | 0.00373 | Blockage | 0.00078748 | 3 | 16.23 | 3 | 9 | 2 | 0.06714 | Most common failure mode(s): Contol/signal failure Most common failure mechanism(s): No signal/indication/alarm | Risk: Low to medirum risk for all failure modes Criticality: The highest criticality number for Control/signal failure followed by Erratic output
[5 empty] | Erratic output | 0.0033842 | Control failure | 0.00023624 | 3 | 10.9408 | 3 | 9 | 2 | 0.060916
[5 empty] | Fail to function on demand | 0.0003761 | Electricl failure-general | 0.00031499 | 2 | 0.75583 | 1 | 2 | 2 | 0.0015044
[5 empty] | Other | 0.00010973 | Faulty signal/indication/alamr | 0.00086623 | 2 | 0 | 1 | 2 | 2 | 0.00043892
[5 empty] | Spurious operation | 0.00027475 | Instrument failure-general | 0.0010237 | 2 | 0 | 1 | 2 |  | 0.001099
[7 empty] | No signal/indication/alarm | 0.0011812
[7 empty] | Out of adjustment | 0.00031499
[7 empty] | Unknown | 0.00047249
|  |  |  | 1 |  | 0.0078748 |  | 0.0051974 | [5 empty] | 0.1311
| Valve positioning sensor | 0.018816 | Valve position sensor | 1 | Control/signal failure | 0.016504 | Blockage | 0.00047039 | 4 | 19.415 | 2 | 8 | 3 | 0.3961 | Most common failure mode(s): Contol/signal failure Most common failure mechanism(s): Faulty signal/indication/alarm signal/indication/alarm | Risk: Low to medium Criticality: The failure mode of Control/signal failure has the highest criticality number
[5 empty] | Erratic output | 0.0014317 | Control failure | 0.0018816 | 3 | 3.9167 | 3 | 9 | 2 | 0.02577
[5 empty] | Plugged/chocked | 0.00045308 | Electrical failure-general | 0.00047039 | 2 | 0.041667 | 1 | 2 | 3 | 0.0027185
[5 empty] | Spurious operation | 0.00042688 | Faulty signal/indication/alarm | 0.01176 | 2 | 0 | 1 | 2 | 2 | 0.0017075
[7 empty] | Instrument failure-general | 0.00037444
[7 empty] | Out of adjustment | 0.00047039
|  |  |  | 1 |  | 0.018816 |  | 0.015427 | [5 empty] | 0.42629
| Programmable Logic Controller (PLC) | 0.1356 | CPU | 0.087 | Fail to function on demand | 0.01651 | Clearance/alignment failure | 0.011797 | 4 | 0.125 | 1 | 4 | 2 | 0.13208 | Most common part(s) failure: Other followed by Subunit Most common failure mode(s): Minor in-service problem Most common failure mechanism(s): Faulity signal/indicaiton/alarm | Risk: Low risk rank for all parts Criticality: The failure modes of Sporious operation has the highest criticality number followed by Minor-in-servcie problems
|  |  | Input card | 0.087 | Low output | 0.020467 | Control failure | 0.01177 | 4 | 2.1662 | 1 | 4 | 2 | 0.16373
|  |  | Other | 0.3479 | Minor in-service problems | 0.063568 | Earth/isolation fault | 0.011797 | 4 | 1.8958 | 1 | 4 | 1 | 0.25427
|  |  | Software | 0.0435 | Spurious operation | 0.035053 | Fault power/voltage | 0.011797 | 4 | 1.0212 | 1 | 4 | 2 | 0.28042
|  |  | Subunit | 0.261 |  |  | Faulty signal/indication/alarm | 0.035377
|  |  | Unkown | 0.0435 |  |  | Instument failure-general | 0.011797
|  |  | Watchdog/dianostics | 0.1304 |  |  | Looseness | 0.011797
[7 empty] | No cause found | 0.0058985
[7 empty] | No power/voltage | 0.0058985
[7 empty] | Software/voltage | 0.011797
[7 empty] | Unknown | 0.0058985
|  |  |  | 1.0003 |  | 0.1356 |  | 0.13562 | [5 empty] | 0.83051
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Side loading occurs when a mass or external force pushes the rod to the side, up or down. from: https://www.fluidpowerworld.com/how-do-hydraulic-cylinders-fail-side-loads/#:~:text=Side%20loading%20occurs%20when%20a,itself%20inside%20the%20cylinder%20bore.

## AllReaction&Stationing
Sub-system | Component | Annual Failure Rate | Part | Failure rate ratio for parts | Failure mode | Annual failure rate | FailureMechanism | Annual failure rate due to the failure mechanism | Occurance (O) | Manhour repair | Severity (S) | Risk priority (O*S) | Failure effect ranking | Criticality number | Summary (Part, Failure modes, Failure mechnisms) | Note & Recommendation
Reaction & Stationing | Fiber Rope | 0.02 | Rope | 0.4 | Material Failure | 0.02 | Fatigue | 0.0058 | 4 |  | 3 | 12 | 3 | 0.72 | Most common part failure: Bearing Dominant failure modes: Surface damage, Fracture/separation Dominant failure mechanism: Wear, Fatigue | Risk: Medium risk
|  |  | Termination Point | 0.6 |  |  | Creep | 0.0058
[7 empty] | Wear | 0.0058
[7 empty] | Ultimate Limit State Tension | 0.0014
[7 empty] | Accidental Limit State Tension | 0.0002
[7 empty] | Capacity Reduction | 0.001
|  | Sum |  |  |  | 0.02 |  | 0.02 | [5 empty] | 0.72
| Chain | 0.02 | Link | 0.4 | Material Failure | 0.02 | Fatigue | 0.0058 | 5 |  | 3 | 12 | 3 | 0.72 |  | Risk: Low to medirum risk for all failure modes Criticality: The highest criticality number for Electrical failure mode followed by Sorious stop
|  |  | Termination Point | 0.6 |  |  | Corrosion | 0.008
[7 empty] | Wear | 0.0036
[7 empty] | ULS Tension | 0.0014
[7 empty] | ALS Tension | 0.0002
[7 empty] | Capacity Reduction | 0.001
|  |  |  | 1 |  | 0.02 |  | 0.02 | [5 empty] | 0.72
| Joints & Connections | 0.1 | Body | 0.05 | Material Failure | 0.1 | Fatigue | 0.025 | 4 |  | 3 | 12 | 3 | 3.6
|  |  | Connection Point | 0.05 |  |  | Corrosion | 0.025
[7 empty] | Marine Growth | 0.035
[7 empty] | ULS Load | 0.01
[7 empty] | ALS Load | 0.001
[7 empty] | Capacity Reduction | 0.004
|  |  |  | 0.1 |  | 0.1 |  | 0.1 | [5 empty] | 3.6
| Floating Support Structure | 0.0061 | Primary Member | 0.00183 | Instability | 0.000915 | Fatigue | 0.001525 | 2 |  | 3 | 6 | 3 | 0.01647 | Most common part(s) failure: Primary Member followed by Connetion points to PTO/Hydrodynamic System Most common failure mode(s): Loss of support Most common failure mechanism: Ultimate limit state | Risk: Low risk rank for all parts Criticality: The failure modes of Sporious operation has the highest criticality number followed by Minor-in-servcie problems
|  |  | Secondary Members | 0.00061 | Change in Bouyancy | 0.000915 | Corrosion | 0.0009455 | 2 |  | 3 | 6 | 2 | 0.01098
|  |  | Connection Points to PTO/HS | 0.001525 | Change in Hydrodynamic Properties | 0.000915 | Wear | 0.0001525 | 2 |  | 2 | 4 | 2 | 0.00732
|  |  | Foundation | 0.000915 | Loss of Support | 0.003355 | Ultimate Limit State | 0.002745 | 3 |  | 5 | 15 | 3 | 0.15098
|  |  | Water tight cavities and ballast tank | 0.00122 |  |  | Accidental Limit State Load Limit | 0.00061
[7 empty] | Capacity Reduction | 0.0001525
|  |  |  | 0.0061 |  | 0.0061 |  | 0.0061305 | [5 empty] | 0.18575
| Fixed Support Structure | 0.0007 | Primary Member | 0.4 | Loss of Support | 0.0007 | Fatigue | 0.00021 | 2 |  | 5 | 10 | 3 | 0.021
|  |  | Secondary Members | 0.1 |  |  | Corrosion | 0.000175
|  |  | Connection Points to PTO/HS | 0.3 |  |  | Wear | 0.000105
|  |  | Foundation | 0.1 |  |  | ULS Load | 7e-06
|  |  | Water tight cavities and ballast tank | 0.1 |  |  | ALS Load | 0.000133
[7 empty] | Capacity Reduction | 7e-05
|  |  |  | 1 |  | 0.0007 |  | 0.0007 | [5 empty] | 0.021
|  | 0.1468 | [11 empty] | 5.2467
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Side loading occurs when a mass or external force pushes the rod to the side, up or down. from: https://www.fluidpowerworld.com/how-do-hydraulic-cylinders-fail-side-loads/#:~:text=Side%20loading%20occurs%20when%20a,itself%20inside%20the%20cylinder%20bore.