## Data Rights Notice
PROTECTED RIGHTS NOTICE
These protected data were produced under agreement no. DE-EE0007347 with the U.S. Department of Energy and may not be published, disseminated, or disclosed to others outside the Government until five (5) years from the date the data were first produced, unless express written authorization is obtained from the recipient. Upon expiration of the period of protection set forth in this Notice, the Government shall have unlimited rights in this data. This Notice shall be marked on any reproduction of this data, in whole or in part.

## 0540 Station Power System
[13 empty] | Risk Ranking | [11 empty] | Updated Risk Ranking | [11 empty] | 2nd Updated Risk Ranking
0540 Station Power System FMECA Table | [13 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class | [7 empty] | Severity Class |  |  |  | Risk Class
Risk ID | Item Description | Function | Tech. Class | Novel Aspects | Failure Mode | Failure Effects (Local, WEC, System) | Failure Cause(s) | Initial Mode of Operation | Risk Reduction Design | Preventative Detection | Post Failure Detection | Post Failure Repair Strategy (automated, manual) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Recommended Actions | Responsible Party | Actions Taken | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | 2nd Recommended Actions | Responsible Party (2nd) | Actions Taken (2nd) | Occurrence | Human Safety | Environment | Operation | Assets | Human Safety | Environment | Operation | Assets | Status (open or closed) | Notes
0541-1 | 480V to 120V transformer | Step down voltage from 0300 electrica plant to provide station utility power for WEC | 1 | none | Electrical fault | 1) Breaker trip power off-line 2) ATB to (port or stbd) source for station power | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance design 2) Redundant design, two station power systems | 1) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 5 | 1 | 1 | 7 | 4 | Low | Low | Med | Low | Check the QC procedures on all component manufacturing.
0541-2 | 480V to 120V transformer | Step down voltage from 0300 electrica plant to provide station utility power for WEC | 1 | none | Electrical fault | 1) Breaker trip power off-line 2) ATB to (port or stbd) source for station power | Improper installation or manufacturing defect results in failure | Normal | 1) V&V (QC) | none | SCADA Diagnostics | Manual in-situ inspection and repair | 5 | 1 | 1 | 7 | 4 | Low | Low | Med | Low | Vibration isolation design for all electric components
0541-3 | 480V to 120V transformer | Step down voltage from 0300 electrica plant to provide station utility power for WEC | 1 | none | Electrical fault | 1) Breaker trip power off-line 2) ATB to (port or stbd) source for station power | Water induced failure (non-corrosion) | Normal | 1)Marine rated waterproof enclosure 2) Redundant design, two station power systems | 1) SCADA diagnostics 2) Visual inspection | SCADA Diagnostics | Manual in-situ inspection and repair | 5 | 1 | 1 | 7 | 4 | Low | Low | Med | Low | Corrosion prevention design for all components
0541-4 | 480V to 120V transformer | Step down voltage from 0300 electrica plant to provide station utility power for WEC | 1 | none | Electrical fault | 1) Breaker trip power off-line 2) ATB to (port or stbd) source for station power | Vibration and/or motion induced failure | Normal | 1) Vibration analysis 2) Equipment and installation designed for dynamic environment 3) Redundant design, two station power systems | none | SCADA Diagnostics | Manual in-situ inspection and repair | 5 | 1 | 1 | 7 | 4 | Low | Low | Med | Low | Waterproofing all components
0541-5 | 480V to 120V transformer | Step down voltage from 0300 electrica plant to provide station utility power for WEC | 1 | none | Electrical fault - smoke/fire | 1) Breaker trip power off-line - electrically isolating transformer 2) ATB to (port or stbd) source for station power | Any of the above 1thru 4 | Normal | 1)Marine rated corrosion resistance design 2) V&V (QC) 3) Redundant design, two station power systems | 1) Inspections | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression | Manual in-situ inspection and repair | 5 | 1 | 1 | 7 | 7 | Low | Low | Med | Med | Waterproofing all components
0542-1 | Switch Gear - Station power breaker | Make/Break station power connection to 480vac bus | 1 | none | Fault - open circuit | 1) Station power powered from other side port/stbd | Corrosion induced failure short circuit | Normal | 1)Marine rated corrosion resistance design 2) V&V (QC) 3) Redundant design, two station power systems | none | 1) SCADA Diagnostics | Manual in-situ repair and inspection | 5 | 1 | 1 | 7 | 5 | Low | Low | Med | Low
0542-2 | Switch Gear - Station power breaker | Make/Break station power connection to 480vac bus | 1 | none | Fault - station power, both breakers fault open | 1) Loss of station power except for critical loads 2) Loss of Cooling and climate control 3) Reduced power until temperature limit 4) Temperature limit = Loss of all AC power | Improper installation or manufacturing defect results in failure | Normal | 1)Marine rated corrosion resistance design 2) V&V (QC) 3) Redundant design, two station power systems | none | 1) SCADA Diagnostics | Manual in-situ repair and inspection | 5 | 1 | 1 | 7 | 5 | Low | Low | Med | Low
0542-3 | Switch Gear - Station power breaker | Make/Break station power connection to 480vac bus | 1 | none | Fault - station power, both breakers fault open | 1) Loss of station power except for critical loads 2) Loss of Cooling and climate control 3) Reduced power until temperature limit 4) Temperature limit = Loss of all AC power | Water induced failure (non-corrosion) | Normal | 1)Marine rated corrosion resistance design 2) V&V (QC) 3) Redundant design, two station power systems | none | 1) SCADA Diagnostics | Manual in-situ repair and inspection | 5 | 1 | 1 | 7 | 5 | Low | Low | Med | Low
0542-4 | Switch Gear - Station power breaker | Make/Break station power connection to 480vac bus | 1 | none | Fault - station power, both breakers fault open | 1) Loss of station power except for critical loads 2) Loss of Cooling and climate control 3) Reduced power until temperature limit 4) Temperature limit = Loss of all AC power | Vibration and/or motion induced failure | Normal | 1)Marine rated corrosion resistance design 2) V&V (QC) 3) Redundant design, two station power systems | none | 1) SCADA Diagnostics | Manual in-situ repair and inspection | 5 | 1 | 1 | 7 | 5 | Low | Low | Med | Low
0542-5 | Switch Gear - Station power breaker | Make/Break station power connection to 480vac bus | 1 | none | Electrical fault - smoke/fire | 1) Loss of station power except for critical loads 2) Loss of Cooling and climate control 3) Reduced power until temperature limit 4) Temperature limit = Loss of all AC power | Any of the above 1thru 4 | Normal | 1)Marine rated corrosion resistance design 2) V&V (QC) 3) Redundant design, two station power systems | none | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression | Manual in-situ repair and inspection | 6 | 1 | 1 | 7 | 7 | Low | Low | Med | Med
0543-1 | Power distribution to Auxiliary System | distribute power to all auxiliary systems | 1 | none | Electrical fault | 1) Loss of UPS | 1) Corrosion induced failure short circuit 2) Water induced failure 3) Vibration induced failure 4) Improper installation | Normal | 1) Marine design and installation 2) V&V (QC) | 1) SCADA diagnostics 2) Visual inspection | 1) SCADA Diagnostics | Manual in-situ repair and inspection | 3 | 1 | 1 | 7 | 5 | Low | Low | Low | Low
0543-2 | Power distribution to Auxiliary System | distribute power to all auxiliary systems | 1 | none | Electrical fault - smoke/fire | 1) Loss of UPS | 1) Corrosion induced failure short circuit 2) Water induced failure 3) Vibration induced failure 4) Improper installation | Normal | 1) Marine design and installation 2) V&V (QC) | 1) SCADA diagnostics 2) Visual inspection | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression | Manual in-situ repair and inspection | 5 | 1 | 1 | 7 | 7 | Low | Low | Med | Med
0544-1 | UPS system | Provide battery back-up uninterruptible power to critical loads | 1 | none | Electrical fault | 1) Loss of UPS | 1) Corrosion induced failure short circuit 2) Water induced failure 3) Vibration induced failure 4) Improper installation | Normal | 1) Marine design and installation 2) V&V (QC) | 1) SCADA diagnostics 2) Visual inspection | 1) SCADA Diagnostics | Manual in-situ repair and inspection | 3 | 1 | 1 | 7 | 5 | Low | Low | Low | Low
0544-2 | UPS system | Provide battery back-up uninterruptible power to critical loads | 1 | none | Electrical fault - following a loss of all AC Power | 1) Loss of UPS 2) Loss of all WEC Power | 1) Corrosion induced failure short circuit 2) Water induced failure 3) Vibration induced failure 4) Improper installation | Emergency - using UPS power | 1) Marine design and installation 2) V&V (QC) | 1) SCADA diagnostics 2) Visual inspection | 1) SCADA Diagnostics | Manual in-situ repair and inspection | 3 | 1 | 1 | 7 | 5 | Low | Low | Low | Low
0544-3 | UPS system | Provide battery back-up uninterruptible power to critical loads | 1 | none | Electrical fault - following a loss of all AC Power | 1) Loss of UPS 2) Loss of all WEC Power | 1) Corrosion induced failure short circuit 2) Water induced failure 3) Vibration induced failure 4) Improper installation | Normal | 1) Marine design and installation 2) V&V (QC) | 1) SCADA diagnostics 2) Visual inspection | 1) Smoke alarms - reduce time to electrically isolate 2) Over-current protection - for electrical isolation 3) Automatic fire suppression | Manual in-situ repair and inspection | 6 | 1 | 1 | 7 | 7 | Low | Low | Med | Med

## version history
Title | StingRAY Station Power FMECA
Doc No | SR-0540-RR
Version | 3.0
Authored | J Prudell
Reviewed
Approved Dist.
Approved Final
Version | Date | Summary
1.0 | 2013-11-08 | Preliminary, not released
1.1 | 2014-01-28 | Preliminary, not released
2.0 | 2016-02-01 | released to RC for review
3.0 | 2016-07-25 | Updated risk matrix, updated for WEC v3.3 technology
The following contains PROTECTED DATA of Columbia Power Technologies, Inc. not for distribution.

## set up
| Risk = Occ + Sev | [11 empty] | Note:
| Severity | [11 empty] | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
10 | Low | Med | Med | Med | Med | High | High | High | High | High
9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11
8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15
7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High
6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High
5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med
4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med |  | Low | Tolerable, no engineer action required
3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med |  | Med | Undesirable, consider engineer actions to mitigate risk
2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med |  | High | Intolerable, engineering action required
1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low
Occurrence | [5 empty] | Severity
Rating | Occurrence |  | Annual Failure Rate | Return Period [years] |  | Rating | Severity | Human Safety |  | Environment |  | WEC Operation |  | Assets
1 | Exceptionally unlikely to occur |  | 1e-05 | 100000 |  | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) |  | Negligible pollution or no effect on environment |  | Negligible effect on performance |  | Negligible
2 |  |  | 3.1623e-05 | 31600 |  | 2 | [7 empty] | [1.5k USD]
3 | Extremely unlikely to occur |  | 0.0001 | 10000 |  | 3 | Minor | Minor injuries, health effects (e.g. stitches) |  | Minor pollution / slight effect on environment (min disruption on marine life) |  | Minor system degradation |  | Repairable in-situ, at next maintenance interval [5k USD]
4 |  |  | 0.00031623 | 3160 |  | 4 |  | Moderate injuries and/or health effects (e.g. broken bone) |  |  |  | Moderate system degradation (e.g. loss of MoMo) |  | Repairable in-situ, outside maintenance interval (1 day) [15k USD]
5 | Very unlikely to occur |  | 0.001 | 1000 |  | 5 | Major |  |  | Limited levels of pollution, manageable / moderate effect on environment |  |  |  | Repairable in-situ, outside maintenance interval (1 week) [50k USD]
6 |  |  | 0.0031623 | 316 |  | 6 | [5 empty] | Major system degradation or loss of operation for 1 month |  | [150k USD]
7 | Rarely expected to occur |  | 0.01 | 100 |  | 7 | Critical | Hospitalization (with full recovery) |  | Moderate pollution (some clean-up costs) / Serious effect on environment |  | Major system degradation or loss of operation for 3 months |  | Dry dock required for repair [500k USD]
8 |  |  | 0.031623 | 31.6 |  | 8 | [5 empty] | Critical system degradation or loss of operation for 6 months |  | [1.5M USD]
9 | One or more during 20 yr lifetime |  | 0.1 | 10 |  | 9 | Catastrophic | Hospitalization (with lasting disabilities) |  | Major pollution (significant clean-up costs) / disastrous effects on the environment |  | Failure to generate power for remainder of project, complete failure |  | Loss of device [5M USD]
10 |  |  | 0.31623 | 3.16 |  | 10 |  | A fatality

## linkedPage
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | Risk = Occ + Sev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Note:
0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - 'set up' and 'linkedPage' are both linked to workbook 'FMECA Master v3.xlsx'
0 | Occ | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | - changes to the tables, risk scores, etc must be made in 'FMECA Master v3.xlsx'
0 | 10 | Low | Med | Med | Med | Med | High | High | High | High | High | 0 | 0 | 0 | 0 | 0
0 | 9 | Low | Low | Med | Med | Med | Med | High | High | High | High | low <= | 11 | 0 | 0 | 0
0 | 8 | Low | Low | Low | Med | Med | Med | Med | High | High | High | high> | 15 | 0 | 0 | 0
0 | 7 | Low | Low | Low | Low | Med | Med | Med | Med | High | High | 0 | 0 | 0 | 0 | 0
0 | 6 | Low | Low | Low | Low | Low | Med | Med | Med | Med | High | 0 | 0 | 0 | 0 | 0
0 | 5 | Low | Low | Low | Low | Low | Low | Med | Med | Med | Med | 0 | 0 | 0 | 0 | 0
0 | 4 | Low | Low | Low | Low | Low | Low | Low | Med | Med | Med | 0 | Low | Tolerable, no engineer action required | 0 | 0
0 | 3 | Low | Low | Low | Low | Low | Low | Low | Low | Med | Med | 0 | Med | Undesirable, consider engineer actions to mitigate risk | 0 | 0
0 | 2 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Med | 0 | High | Intolerable, engineering action required | 0 | 0
0 | 1 | Low | Low | Low | Low | Low | Low | Low | Low | Low | Low | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Occurrence | 0 | 0 | 0 | 0 | 0 | Severity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Rating | Occurrence | 0 | Annual Failure Rate | Return Period [years] | 0 | Rating | Severity | Human Safety | 0 | Environment | 0 | WEC Operation | 0 | Assets | 0
0 | 1 | Exceptionally unlikely to occur | 0 | 1e-05 | 100000 | 0 | 1 | Insignificant | Negligible injury, effect on health (e.g. band aid) | 0 | Negligible pollution or no effect on environment | 0 | Negligible effect on performance | 0 | Negligible | 0
0 | 2 | 0 | 0 | 3.1623e-05 | 31600 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [1.5k USD] | 0
0 | 3 | Extremely unlikely to occur | 0 | 0.0001 | 10000 | 0 | 3 | Minor | Minor injuries, health effects (e.g. stitches) | 0 | Minor pollution / slight effect on environment (min disruption on marine life) | 0 | Minor system degradation | 0 | Repairable in-situ, at next maintenance interval [5k USD] | 0
0 | 4 | 0 | 0 | 0.00031623 | 3160 | 0 | 4 | 0 | Moderate injuries and/or health effects (e.g. broken bone) | 0 | 0 | 0 | Moderate system degradation (e.g. loss of MoMo) | 0 | Repairable in-situ, outside maintenance interval (1 day) [15k USD] | 0
0 | 5 | Very unlikely to occur | 0 | 0.001 | 1000 | 0 | 5 | Major | 0 | 0 | Limited levels of pollution, manageable / moderate effect on environment | 0 | 0 | 0 | Repairable in-situ, outside maintenance interval (1 week) [50k USD] | 0
0 | 6 | 0 | 0 | 0.0031623 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | Major system degradation or loss of operation for 1 month | 0 | [150k USD] | 0
0 | 7 | Rarely expected to occur | 0 | 0.01 | 100 | 0 | 7 | Critical | Hospitalization (with full recovery) | 0 | Moderate pollution (some clean-up costs) / Serious effect on environment | 0 | Major system degradation or loss of operation for 3 months | 0 | Dry dock required for repair [500k USD] | 0
0 | 8 | 0 | 0 | 0.031623 | 31.6 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | Critical system degradation or loss of operation for 6 months | 0 | [1.5M USD] | 0
0 | 9 | One or more during 20 yr lifetime | 0 | 0.1 | 10 | 0 | 9 | Catastrophic | Hospitalization (with lasting disabilities) | 0 | Major pollution (significant clean-up costs) / disastrous effects on the environment | 0 | Failure to generate power for remainder of project, complete failure | 0 | Loss of device [5M USD] | 0
0 | 10 | 0 | 0 | 0.31623 | 3.16 | 0 | 10 | 0 | A fatality | 0 | 0 | 0 | 0 | 0 | 0 | 0